## AC MPR
Brand Name or Equal
|  | Manufacturer: Siemens | Manufacturer: ABB | Manufacturer: ______________________________
_____________________________________________
|  | Basis Part Number (P/N): 7SJ6235 | Basis Part Number (P/N): HAFDDADAAAE1BNN1XE | Basis Part Number (P/N): See technical specifications
|  | Quoted Part Number (P/N): ______________________ | Quoted Part Number (P/N): ______________________ | Quoted Part Number (P/N): ______________________
|  | ____________________________________________________ | ____________________________________________________ | ____________________________________________________
Quoted Part Information:
|  | 1. Are you quoting the basis P/N listed above? (Yes / No) If not, please refer to Note 1. below | 1. Are you quoting the basis P/N listed above? (Yes / No) If not, please refer to Note 1. below | Please refer to Note 1. below
Delivery:
|  | 2. Number of days required for delivery: ______________ ARO | 2. Number of days required for delivery: ______________ ARO | 2. Number of days required for delivery: ______________ ARO
|  | 3a. Delivery lead time for first shipment: _______________ARO | 3a. Delivery lead time for first shipment: _______________ARO | 3a. Delivery lead time for first shipment: _______________ARO
|  | 3b. Product quantity in first shipment: _______________EACH | 3b. Product quantity in first shipment: _______________EACH | 3b. Product quantity in first shipment: _______________EACH
|  | 4a. Delivery lead time for next shipment(s): _______________ADFS | 4a. Delivery lead time for next shipment(s): _______________ADFS | 4a. Delivery lead time for next shipment(s): _______________ADFS
|  | 4b.Product quantity in next shipment(s): _______________EACH | 4b.Product quantity in next shipment(s): _______________EACH | 4b.Product quantity in next shipment(s): _______________EACH
TECHNICAL REQUIREMENTS | WMATA REQUIREMENTS | Complies with Requirements Yes / No | Complies with Requirements Yes / No | Complies with Requirements Yes / No
GENERAL
TYPE | Advanced multifunction microprocessor-based relay | YES or NO | YES or NO | YES or NO
MOUNTING TYPE | Flush Mounting, screw type terminals; The relay design shall include “draw-out” and “draw-in” components where the draw-out unit can be withdrawn or inserted to a fixed mounted case. | YES or NO | YES or NO | YES or NO
DISPLAY | GRAPHIC DISPLAY HMI . The relay shall be provided with easy to use Human-Machine-Interface (HMI) front-panel display, user-interface functionality with menu navigation and menu views. | YES or NO | YES or NO | YES or NO
INPUTS/OUTPUTS | 4 Voltage Inputs | YES or NO | YES or NO | YES or NO
| 4 Current Inputs | YES or NO | YES or NO | YES or NO
| 8 Binary Inputs | YES or NO | YES or NO | YES or NO
| 8 Binary Outputs | YES or NO | YES or NO | YES or NO
| 4 Controls | YES or NO | YES or NO | YES or NO
CONTROL POWER | 125V DC | YES or NO | YES or NO | YES or NO
FRONT MAINTENANCE PORT | RJ-45 Ethernet connector | YES or NO | YES or NO | YES or NO
ENVIRONMENT AND CABINET INFORMATION | Unit shall be packaged in a steel case for transient immunity and structural integrity that is suitable for conventional panel flush mounting or semi flush mounted. | YES or NO | YES or NO | YES or NO
ARC FLASH | Three arc sensors | YES or NO | YES or NO | YES or NO
MONITORING & CONTROL FUNCTIONS
INTEGRATED POWER QUALITY METER | Includes power quality function to continuously measures the phase currents and voltages, calculate the maximum demand value over selected preset time frame, the thermal overload of the protected equipment, the unbalance values and power factor. | YES or NO | YES or NO | YES or NO
ACCURACY | Meet ANSI C12.20 accuracy class 0.2.
EVENT RECORDER | The relay shall collect sequence of events information, incorporates memory with a capacity of storing 50 events with associated time stamps. | YES or NO | YES or NO | YES or NO
DISTURBANCE RECORDER | The relay shall be provided with disturbance recorder featuring up to eight analog and 32 binary signal channels. The analog channels can be set to record ether waveform or the trend of the currents and voltage measured. Waveform Recording- up to 512 sample/cycle | YES or NO | YES or NO | YES or NO
TRIP/CLOSE CONTROL | The relay shall offer control of one circuit breaker with dedicated push-buttons for opening and closing. | YES or NO | YES or NO | YES or NO
FUSE FAILURE SUPERVISION | REQUIRED | YES or NO | YES or NO | YES or NO
CIRCUIT SUPERVISION | The relay shall include trip-circuit supervision continuously monitoring the availability and operability of the trip circuit. | YES or NO | YES or NO | YES or NO
CONTROL FUNCTIONS | REQUIRED | YES or NO | YES or NO | YES or NO
OPERATION TRACEABILITY | REQUIRED | YES or NO | YES or NO | YES or NO
SELF-SUPERVISION | The relay’s built-in self-supervision system continuously monitors the state of the relay hardware and the operation of the relay software. Any fault or malfunction detected will be used for alerting the operator through a fail safe contact. | YES or NO | YES or NO | YES or NO
ACCESS CONTROL | To protect the relay from unauthorized access and to maintain information integrity, the relay shall be provided with a four-level access control. The access control shall apply to the front-panel user interface, the web-browser based user interface. | YES or NO | YES or NO | YES or NO
CIRCUIT BREAKER CONDITION MONITORING | The relay shall constantly monitor the performance and the condition of the circuit breaker. | YES or NO | YES or NO | YES or NO
PROTECTIVE FUNCTIONS
PHASE OVER CURRENT | 50/51 THREE PHASE OVERCURRENT PROTECTION | YES or NO | YES or NO | YES or NO
GROUND FAULT | 50N/51N GROUND-FAULT PROTECTION | YES or NO | YES or NO | YES or NO
FAILURE PROTECTION | 50BF BREAKER FAILURE PROTECTION | YES or NO | YES or NO | YES or NO
TRIP CIRCUIT | 74TC TRIP CIRCUIT SUPERVISION | YES or NO | YES or NO | YES or NO
LOCKOUT | 86 LOCKOUT | YES or NO | YES or NO | YES or NO
UNDER /OVER VOLTAGE | 27/59 THREE PHASE UNDER-/OVERVOLTAGE | YES or NO | YES or NO | YES or NO
FREQUENCY | 81O/U UNDER-/OVER FREQUENCY | YES or NO | YES or NO | YES or NO
SYNCHRO-CHECK | 25 SYNCHRO-CHECK | YES or NO | YES or NO | YES or NO
ANSI RI-9 PROTECTIONS | Three Phase Relay 51A function to protect against overloads beyond the 300 percent, one minute capability of the units. | YES or NO | YES or NO | YES or NO
| Three Phase Relay 51B functions to protect against overloads beyond the 450 percent, 15 second capability of the units and coordinated with relay 51A. | YES or NO | YES or NO | YES or NO
COMMUNICATION & SECURITY FUNCTIONS
COMMUNICATION PROTOCOLS | DNP3 & IEC61850 | YES or NO | YES or NO | YES or NO
COMMUNICATION MODULE | 100BASE-FX with a fiber optic LC or ST | YES or NO | YES or NO | YES or NO
WEB INTERFACE | Web server functionality for remote monitioring; remote access via Ethernet interface using standard web browser | YES or NO | YES or NO | YES or NO
RELAY TIME SYNCHRONIZATION | Relay shall include Network Time Protocol to be configured to time synchronize with WMATA network time servers. | YES or NO | YES or NO | YES or NO
SAFETY AND SECURITY | Access to the MPR parameters shall be time stamped, code protected and shall initiate an alarm on any un- authorized attempt to the set parameters. | YES or NO | YES or NO | YES or NO
SOFTWARE & CONFIGURATION
CONFIGURATION SOFTWARE | Programming software shall be provided with each relay | YES or NO | YES or NO | YES or NO
SOFTWARE LICENSES | Ten (10) fully licensed versions of the programming software shall be provided under this contract. | YES or NO | YES or NO | YES or NO
OTHER REQUIREMENTS
TECHNICAL SUPPORT | Relay manufacturer’s technical services assistance shall be readily available within USA | YES or NO | YES or NO | YES or NO
QUALITY ASSURANCE | Certified design tests completed. Tests as defined in IEEE C37.100.1. | YES or NO | YES or NO | YES or NO
OPERATION MTBF | MEAN TIME BETWEEN FAILURES: FIVE YEARS | YES or NO | YES or NO | YES or NO
Notes: 1.If the part number quoted differs from the part number requested, please provide a letter explaining why; include technical specifications for the quoted product (cut sheet, shop drawing, test results, etc.); also a signed memorandum in PDF format stating you are an authorized distributor for this part. An example memorandum can be provided upon request. ARO - After Receipt of Order ADFS - After Delivery of First Shipment

## DC MPR
Brand Name or Equal
|  | Manufacturer: Siemens | Manufacturer: VG Controls | Manufacturer: Secheron | Manufacturer: ___________________________________
________________________________________________
|  | Basis Part Number (P/N): A2V000221 | Basis Part Number (P/N): MPR E32VG8 | Basis Part Number (P/N): SG824300R1100040 | Basis Part Number (P/N):: See technical specifications
|  | Quoted Part Number (P/N): _______________________ | Quoted Part Number (P/N): _______________________ | Quoted Part Number (P/N): _______________________ | Quoted Part Number (P/N): _______________________
|  | ______________________________________________________ | ______________________________________________________ | ______________________________________________________ | ______________________________________________________
Quoted Part Information:
|  | 1. Are you quoting the basis P/N listed above? (Yes / No) If not, please refer to to Note 1. below | 1. Are you quoting the basis P/N listed above? (Yes / No) If not, please refer to to Note 1. below | 1. Are you quoting the basis P/N listed above? (Yes / No) If not, please refer to to Note 1. below | Please refer to Note 1. below
Delivery:
|  | 2. Number of days required for delivery:______________ARO | 2. Number of days required for delivery:______________ARO | 2. Number of days required for delivery:______________ARO | 2. Number of days required for delivery:______________ARO
|  | 3a. Delivery lead time for first shipment: _______________ARO | 3a. Delivery lead time for first shipment: _______________ARO | 3a. Delivery lead time for first shipment: _______________ARO | 3a. Delivery lead time for first shipment: _______________ARO
|  | 3b. Product quantity in first shipment: _______________EACH | 3b. Product quantity in first shipment: _______________EACH | 3b. Product quantity in first shipment: _______________EACH | 3b. Product quantity in first shipment: _______________EACH
|  | 4a. Delivery lead time for next shipment(s): _______________ADFS | 4a. Delivery lead time for next shipment(s): _______________ADFS | 4a. Delivery lead time for next shipment(s): _______________ADFS | 4a. Delivery lead time for next shipment(s): _______________ADFS
|  | 4b.Product quantity in next shipment(s): _______________EACH | 4b.Product quantity in next shipment(s): _______________EACH | 4b.Product quantity in next shipment(s): _______________EACH | 4b.Product quantity in next shipment(s): _______________EACH
TECHNICAL REQUIREMENTS | WMATA REQUIREMENTS | Complies with Requirements Yes / No | Complies with Requirements Yes / No | Complies with Requirements Yes / No | Complies with Requirements Yes / No
GENERAL
TYPE | Advanced multifunction microprocessor-based relay | YES or NO | YES or NO | YES or NO | YES or NO
MAIN MODULE MOUNTING TYPE | Surface Mounting, connected to transducer by Fiber glass cable. | YES or NO | YES or NO | YES or NO | YES or NO
DISPLAY | GRAPHIC DISPLAY HMI: The relay shall be provided with easy to use Human-Machine-Interface (HMI) front-panel display or LCD, user-interface functionality with menu navigation and menu views. Flush Mounting. | YES or NO | YES or NO | YES or NO | YES or NO
INPUTS/OUTPUTS | 2 Voltage Inputs Through voltage transducer: Line Side & Load Side | YES or NO | YES or NO | YES or NO | YES or NO
| 1 Current Input : From DC shunt thorugh Current transducer | YES or NO | YES or NO | YES or NO | YES or NO
| Minimum of 16 Input Contacts | YES or NO | YES or NO | YES or NO | YES or NO
| Minimum of 16 Output Contacts | YES or NO | YES or NO | YES or NO | YES or NO
| Minimum of 6 Control Contacts | YES or NO | YES or NO | YES or NO | YES or NO
CONTROL POWER | 125 Volts dc +/- 10%, 10 VA (Max) | YES or NO | YES or NO | YES or NO | YES or NO
MAINTENANCE PORT | RJ-45 Ethernet connector | YES or NO | YES or NO | YES or NO | YES or NO
ENVIRONMENT INFORMATION | MPR and the associated components shall be designed for extremely harsh environmental (dusty, humid) conditions. | YES or NO | YES or NO | YES or NO | YES or NO
| Temperature Test: Per IEEE 37.90. Temperature Range : -5°C to + 55°C | YES or NO | YES or NO | YES or NO | YES or NO
| Humidity Test: Per IEEE 37.90. | YES or NO | YES or NO | YES or NO | YES or NO
| All MPR relays, associated components and ancillary equipment shall be rated for continuous operation in this environment. | YES or NO | YES or NO | YES or NO | YES or NO
| Equipment shall function as intended when subjected to all electromagnetic interference present in the vicinity of 750 V DC power circuits and traction power equipment. | YES or NO | YES or NO | YES or NO | YES or NO
ACCURACY | + 0.5% Rated Output @ 25°C | YES or NO | YES or NO | YES or NO | YES or NO
MONITORING & CONTROL FUNCTIONS
MEASUREMENT FUNCTIONS | The MPR shall provide current measurement. | YES or NO | YES or NO | YES or NO | YES or NO
| The MPR shall provide Line and load side voltage measurements. | YES or NO | YES or NO | YES or NO | YES or NO
| The MPR shall provide Load side impedance measurement. | YES or NO | YES or NO | YES or NO | YES or NO
CONTROL FUNCTIONS | The MPR shall provide for closing and opening of the breakers when commanded. | YES or NO | YES or NO | YES or NO | YES or NO
| The MPR shall trip the feeder breaker on detection of the faults | YES or NO | YES or NO | YES or NO | YES or NO
| The MPR shall initiate automatic reclosing of the tripped circuit breaker upon detection of acceptance impedance and voltage conditions. | YES or NO | YES or NO | YES or NO | YES or NO
| The relays shall be capable to received and execute controls | YES or NO | YES or NO | YES or NO | YES or NO
| The MPR shall have transfer trip capability. | YES or NO | YES or NO | YES or NO | YES or NO
MONITORING FUNCTIONS | The MPR shall have self –diagnostics capability | YES or NO | YES or NO | YES or NO | YES or NO
| The MPR shall monitor circuit breaker health | YES or NO | YES or NO | YES or NO | YES or NO
| The MPR shall monitor and provide breaker status | YES or NO | YES or NO | YES or NO | YES or NO
| Shall be capable of streaming breaker line voltage, load voltage and current to SCADA | YES or NO | YES or NO | YES or NO | YES or NO
| The relay shall include webserver for remote access via standard web browser. | YES or NO | YES or NO | YES or NO | YES or NO
| The relay shall include digital output connected to external device | YES or NO | YES or NO | YES or NO | YES or NO
| The MPR shall monitor Under and over voltage conditions. | YES or NO | YES or NO | YES or NO | YES or NO
| The relay shall constantly monitor the performance and the condition of the circuit breaker. | YES or NO | YES or NO | YES or NO | YES or NO
PROTECTIVE FUNCTIONS
INSTANTANEOUS FAULTS | Shall provide bi-directional intantaneous fault protection to the equipment. | YES or NO | YES or NO | YES or NO | YES or NO
REVERSE CURRENT FAULTS | Shall provide reverse current protection for rectifiers | YES or NO | YES or NO | YES or NO | YES or NO
LOW LEVEL FAULTS | Shall provide bi-directional Low Level fault protection to the equipment. | YES or NO | YES or NO | YES or NO | YES or NO
TIMED OVERCURRENT FAULTS | Shall provide bi-directional Timed Overcurrent fault protection to the equipment. | YES or NO | YES or NO | YES or NO | YES or NO
RATE OF RISE FAULTS | Shall be capable to as distinct the faults current from the train start and switching of the train auxiliaries to avoid nuisance tripping of the feeder breakers | YES or NO | YES or NO | YES or NO | YES or NO
LONG TIME OVERCURRENT FAULTS | 3. Shall provide protection to the cable against thermal over loads. | YES or NO | YES or NO | YES or NO | YES or NO
TRANSFER TRIP INITIATE | shall include capability for transfer trip due to forward and Reverse faults | YES or NO | YES or NO | YES or NO | YES or NO
COMMUNICATION & SECURITY FUNCTIONS
COMMUNICATION PROTOCOLS | DNP3 or Modbus or IEC61850 | YES or NO | YES or NO | YES or NO | YES or NO
COMMUNICATION MODULE | 100BASE-FX with a fiber optic LC or ST | YES or NO | YES or NO | YES or NO | YES or NO
WEB INTERFACE | Web server functionality for remote monitioring; remote access via Ethernet interface using standard web browser | YES or NO | YES or NO | YES or NO | YES or NO
SYSTEM FAILURE ALARM | The relay’s built-in self-supervision system continuously monitors the state of the relay hardware and the operation of the relay software. Any fault or malfunction detected will be used for alerting the operator through a fail safe dry contact. | YES or NO | YES or NO | YES or NO | YES or NO
RELAY TIME SYNCHRONIZATION | Relay shall include Network Time Protocol to be configured to time synchronize with WMATA network time servers. | YES or NO | YES or NO | YES or NO | YES or NO
SAFETY AND SECURITY | Access to the MPR parameters shall be time stamped, code protected and shall initiate an alarm on any un- authorized attempt to the set parameters. | YES or NO | YES or NO | YES or NO | YES or NO
ADDITIONAL FEATURES
RELAY SYSTEM | The MPR Ssystem shall include all hardware, software, and ancillary circuits connecting between the various equipment modules so as to implement the protection, indication, load measuring, automatic reclosing functions and monitoring functions | YES or NO | YES or NO | YES or NO | YES or NO
EVENT RECORDER | The MPR shall include an Event Time Recorder to record peak current values prior to and during the operation of relay during fault conditions. | YES or NO | YES or NO | YES or NO | YES or NO
ISOLATOR/ AMPLIFIERS | The MPR shall include the isolator/ amplifiers and other hardware complete to perform its intended functions. | YES or NO | YES or NO | YES or NO | YES or NO
SYSTEM FAILURE ALARM | The relay’s built-in self-supervision system continuously monitors the state of the relay hardware and the operation of the relay software. Any fault or malfunction detected will be used for alerting the operator through a fail safe dry contact. | YES or NO | YES or NO | YES or NO | YES or NO
EVENT LOGGER | The relay shall include event log with time stamp for all protective functions and critical alarm monitoring functions included in the relay | YES or NO | YES or NO | YES or NO | YES or NO
SAFETY AND SECURITY | Access to the MPR parameters shall be time stamped, code protected and shall initiate an alarm on any un- authorized attempt to the set parameters. | YES or NO | YES or NO | YES or NO | YES or NO
SOFTWARE & CONFIGURATION
CONFIGURATION SOFTWARE | Programming software shall be provided with each relay | YES or NO | YES or NO | YES or NO | YES or NO
SOFTWARE LICENSES | Ten (10) fully licensed versions of the programming software shall be provided under this contract. | YES or NO | YES or NO | YES or NO | YES or NO
OTHER REQUIREMENTS
TECHNICAL SUPPORT | Relay manufacturer’s technical services assistance shall be readily available within USA | YES or NO | YES or NO | YES or NO | YES or NO
QUALITY ASSURANCE | Certified design tests completed. Tests as defined in IEEE C37.100.1. | YES or NO | YES or NO | YES or NO | YES or NO
OPERATION MTBF | MEAN TIME BETWEEN FAILURE: 100000 HRS. | YES or NO | YES or NO | YES or NO | YES or NO
Notes: 1.If the part number quoted differs from the part number requested, please provide a letter explaining why; include technical specifications for the quoted product (cut sheet, shop drawing, test results, etc.); also a signed memorandum in PDF format stating you are an authorized distributor for this part. An example memorandum can be provided upon request. ARO - After Receipt of Order ADFS - After Delivery of First Shipment

## PQM
Manufacturer: _______________________________
____________________________________________
Basis Part Number (P/N): Siemens - 7SJ6235
Quoted Part Number (P/N): ____________________
___________________________________________________
Quoted Part Information:
1. Are you quoting the basis P/N listed above? (Yes / No) If not, please refer to Note 1. below
Delivery:
2. Number of days required for delivery: ______________ ARO
3a. Delivery lead time for first shipment: _______________ARO
3b. Product quantity in first shipment: _______________EACH
4a. Delivery lead time for next shipment(s): _______________ADFS
4b.Product quantity in next shipment(s): _______________EACH
TECHNICAL REQUIREMENTS | WMATA REQUIREMENTS | Complies with Requirements Yes / No
GENERAL
TYPE | Advanced multifunction microprocessor-based relay | YES or NO
MOUNTING TYPE | The meter case shall be aluminum with a front-panel International Protection (IP) rating of 65 when installed in a panel. Mounting provisions shall include rack-, panel-, flush and surface-mount options. | YES or NO
Conformal Coating. | The circuit boards in the device shall include conformal coating for harsh environments. | YES or NO
DISPLAY | GRAPHIC DISPLAY HMI . Integrated liquid crystal display (LCD) shall report all available analog quantities including power, energy, voltage, current, frequency, harmonics, phase angle, and maximum/minimum values Programmable LEDs shall indicate status, alarms, and the presence of voltage. | YES or NO
INPUTS/OUTPUTS | 4 Voltage Inputs | YES or NO
| 5 Current Inputs | YES or NO
| Shall sample at 1024 or 512 samples per cycle. | YES or NO
| Shall be able to accept 600VAC LL / 347VAC LN without using potential transformers. | YES or NO
| Three electromechanical outputs | YES or NO
| Two digital inputs | YES or NO
CONTROL POWER | 125V DC | YES or NO
FRONT MAINTENANCE PORT | RJ-45 Ethernet connector | YES or NO
ENVIRONMENT AND CABINET INFORMATION | Shall operate over a temperature range of -20° C to 70° C | YES or NO
| Unit shall be packaged in a steel case for transient immunity and structural integrity that is suitable for conventional panel flush mounting or semi flush mounted. | YES or NO
ARC FLASH | Three arc sensors | YES or NO
MONITORING & CONTROL FUNCTIONS
ACCURACY | Meet ANSI C12.20 accuracy class 0.2. | YES or NO
MINIMUM/MAXIMUM RECORDING | Each phase voltage and current shall have the date and time of the last maximum and minimum value since resetting the maximum/minimum. | YES or NO
SEQUENTIAL EVENTS RECORDER | A chronological report shall record the most recent 16,000 events with 1 ms time-stamp accuracy. | YES or NO
VOLTAGE SAG/SWELL/INTERRUPTION RECORDING | shall capture excursions with 1 ms time-stamp accuracy. At least 11,000 record samples shall adapt sampling rates from a quarter cycle to daily | YES or NO
Waveform Capture | The meter shall simultaneously capture 512 samples-per-cycle events for a total of 35 seconds from each phase. | YES or NO
Harmonic Metering | Shall report individual harmonics up to the 63rd order, including voltage, current, phase angles, and power magnitudes | YES or NO
Logging and alarming | The power quality meter shall log measured parameters, PQ disturbances, events and alarms, and input status. It shall have an event log, time-stamped to the millisecond. | YES or NO
Time-of-Use (TOU) Metering | The meter shall record demand and energy consumption during different time periods based on a user-defined calendar. | YES or NO
Analog and Math Logic | Binary and analog meter data shall be available for Boolean logic calculations and mathematical functions | YES or NO
ACCESS CONTROL | To protect the relay from unauthorized access and to maintain information integrity, the relay shall be provided with a four-level access control. The access control shall apply to the front-panel user interface, the web-browser based user interface. | YES or NO
COMMUNICATION & SECURITY FUNCTIONS
COMMUNICATION PROTOCOLS | DNP3 & IEC61850 | YES or NO
COMMUNICATION MODULE | 100BASE-FX with a fiber optic LC or ST | YES or NO
WEB INTERFACE | Web server functionality for remote monitioring; remote access via Ethernet interface using standard web browser | YES or NO
TIME SYNCHRONIZATION | Relay shall include Network Time Protocol to be configured to time synchronize with WMATA network time servers. | YES or NO
SAFETY AND SECURITY | Access to the MPR parameters shall be time stamped, code protected and shall initiate an alarm on any un- authorized attempt to the set parameters. | YES or NO
SOFTWARE & CONFIGURATION
CONFIGURATION SOFTWARE | Programming software shall be provided with each relay | YES or NO
SOFTWARE LICENSES | Ten (10) fully licensed versions of the programming software shall be provided under this contract. | YES or NO
OTHER REQUIREMENTS
TECHNICAL SUPPORT | Relay manufacturer’s technical services assistance shall be readily available within USA | YES or NO
FACTORY CALIBRATION REPORT | All meters shall be tested in factory for accuracy at quarter, half, three quarters and full range points. | YES or NO
compliance certification for IEC62053-22 | The power monitoring instrument shall have third-party compliance certification for IEC62053-22: Electricity metering equipment (AC) | YES or NO
QUALITY ASSURANCE | Certified design tests completed. Tests as defined in IEEE C37.100.1. | YES or NO
OPERATION MTBF | MEAN TIME BETWEEN FAILURES: FIVE YEARS | YES or NO
Notes: 1.If the part number quoted differs from the part number requested, please provide a letter explaining why; include technical specifications for the quoted product (cut sheet, shop drawing, test results, etc.); also a signed memorandum in PDF format stating you are an authorized distributor for this part. An example memorandum can be provided upon request. ARO - After Receipt of Order ADFS - After Delivery of First Shipment